SECTION 02080

UTILITY PIPE AND MATERIALS

PART 1 - GENERAL

1.1	Description

1.	Work Included:  The work in this section shall include the furnishing, installation, and testing of all pipe, fittings and structures, and furnishing the equipment, labor, and appurtenances for the installation of piped utilities.  All work shall be completed as shown on the plans and as specified in related sections and hereunder.

2.	Related Sections:  Additional Sections of the Documents which are referenced in this Section Include:

1)	Section 02085 - Valves and Cocks

2)	Section 02317- Excavating, Trenching, and Backfilling for Utilities

3)	Section 02510 - Water Distribution

1.2	references

1.	General:  The Work shall comply with the most recent or tentative standards as published at the date of the Contract and as listed in the Specifications using abbreviations shown.

2.	American Association of State Highway and Transportation Officials Publications (AASHTO):

1)	M 252	Corrugated Polyethylene Drainage Tubing

2)	M 294	Corrugated Polyethylene Pipe 12- to 24-in. in Diameter

3.	American Society for Testing and Materials (ASTM):

1)	A 48	Standard Specification for Gray Iron Castings

2)	A 123	Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

3)	A 153	Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware

4)	A 307	Standard Specification for Carbon Steel Bolts and Studs, 60,000 psi Tensile

5)	A 449	Standard Specification for Quenched and Tempered Steel Bolts and Studs

6)	A 536	Standard Specification for Ductile Iron Castings

7)	A 563	Standard Specification for Carbon and Alloy Steel Nuts

8)	B 88	Standard Specification for Seamless Copper Water Tube

9)	C 443	Standard Specification for Joints for Concrete Pipe and Manholes, Using Rubber Gaskets

10)	C 478	Standard Specification for Precast Reinforced Concrete Manhole Sections

11)	C 1173	Standard Specification for Flexible Transition Couplings for Underground Piping Systems

12)	C 1244	Standard Test Method for Concrete Sewer Manholes by Negative Air Pressure (Vacuum) Test Prior to Backfill

13)	D 1149	Standard Test Method for Rubber Deterioration-Surface Ozone Cracking in a Chamber

14)	D 1784	Standard Specification for Rigid Poly (Vinyl Chloride) (PVC) Compounds and Chlorinated Poly (Vinyl Chloride) CPVC Compounds.

15)	D 1785	Standard Specification for Poly (Vinyl Chloride) Plastic Pipe, Schedules 40, 80, and 120

16)	D 2241	Standard Specification for Poly(Vinyl Chloride)(PVC) Pressure-Rated Pipe (SDR Series)

17)	D 2321	Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications

18)	D 2412	Standard Test Method for Determination of External Loading Characteristics of Plastic Pipe by Parallel-Plate Loading.

19)	D 2466	Standard Specification for Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40

20)	D 2564	Standard Specification for Solvent Cements for Poly (Vinyl Chloride) (PVC) Plastic Piping Systems

21)	D 3212	Standard Specification for Joints for Drain and Sewer Plastic Pipes Using Flexible Elastometric Seals

22)	D 5926	Standard Specification for Poly (Vinyl Chloride) (PVC) Gaskets for Drain, Waste, and Vent (DWV), Sewer, Sanitary, and Storm Plumbing Systems

23)	F 405	Standard Specification for Corrugated Polyethylene (PE) Tubing and Fittings

24)	F 477	Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe

25)	F 493	Standard Specification for Solvent Cements for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe and Fittings

26)	F 667	Standard Specification for Large Diameter Corrugated Polyethylene Pipe and Fittings

27)	F 1417	Standard Test Method for Installation Acceptance of Plastic Gravity Sewer Lines Using Low-Pressure Air

4.	American National Standard Institute (ANSI)/American Water Works Association (AWWA):

1)	C 104	Standard for Cement-Mortar Lining for Ductile-Iron Pipe and Fittings for Water

2)	C 110	Standard for Ductile-Iron and Gray-Iron Fittings

3)	C 111	Standard for Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

4)	C 150	Standard for Thickness Design of Ductile-Iron Pipe

5)	C 151	Standard for Ductile-Iron Pipe, Centrifugally Cast, for Water

6)	C 153	Standard For Ductile-Iron Compact Fittings, 3 In. Through 24 In. (76 mm Through 610 mm) and 54 In. Through 64 In. (1,400 mm Through 1,600 mm), For Water Service

7)	C 220	Standard for Stainless Steel Pipe 4 inches (100 mm) and Larger (Includes Addendum C 220a-99)

8)	C 600	Standard for Installation of Ductile-Iron Water Mains and their Appurtenances

9)	C 605	Standard for Underground Installation of Polyvinyl Chloride (PVC) Pressure Pipe and Fittings for Water

5.	Safety Codes Commission, Commonwealth of Virginia:

1)	Rules and Regulations Governing Manufacture, Storage, Use, and Sale of Explosives.

6.	Virginia Department of Transportation - Road and Bridge Specifications (VDOT):

1)	217	Hydraulic Cement Concrete

2)	232	Pipe and Pipe Arches

3)	302	Drainage Structures

1.3	QUALITY ASSURANCE

1.	Quality Assurance:  All pipe and fittings shall be new, free from defects or contamination and shall, whenever possible, be the standard product of a single manufacturer.

2.	Manufacturers Limitations:  Products used in the work of this section shall be manufactured in the U.S. where possible by manufacturers regularly engaged in production of similar items.

1.4	SUBMITTALS

1.	General:  Submittals shall be in accordance with Division I requirements.

1.5	DELIVERY, storage and handling

1.	General:  Delivery, Storage, and Handling shall be in accordance with Division I requirements.

Part 2 - products

2.1	PIPE

1.	Polyvinyl Chloride (PVC) Pipe:  Polyvinyl chloride pipe shall be made from clean, virgin, PVC compound conforming to ASTM D 1784, and meet the following requirements:

1)	Gravity Sewer Pipe:  Pipe shall be SDR 35 bell and spigot conforming to ASTM D 3034 with a rubber sealing ring locked in place to allow expansion and contraction but prevent displacement during assembly.  Pipe stiffness at 5 percent deflection shall exceed 46 psi when tested in accordance with ASTM D 2412.  Joints shall be designed to pass when tested in accordance with ASTM D 3212.

2.	Ductile Iron Pipe:  Ductile iron pipe (DIP) and fittings shall meet or exceed the following requirements:

1)	Pipe and fittings shall be the diameter shown on the plans.

2)	Pressure Class 350 in accordance with AWWA C 150.

3)	Cast in accordance with AWWA C 151.

4)	Cement lining in accordance with AWWA C 104 except on air piping or as otherwise noted.

5)	All lines below grade shall be constructed with push-on joints and mechanical joints at fittings.

3.	Copper Tubing:  All copper tubing shall meet the requirements of ASTM B 88 for Type “K” hard drawn for services.

4.	Corrugated Polyethylene (PE) Drain Pipe (Smooth Bore Type):  Pipe shall be solid high density polyethylene and shall meet the requirements of AASHTO M 294 Type S and of ASTM D 3350 minimum cell classification.

1)	The pipe shall have a smooth interior and annular exterior corrugations. Manning's "n" value for use in design shall not exceed 0.010. Size shall be as indicated on the plans.

2)	Joints: Pipe shall be joined with a bell-and-spigot joint meeting the requirements of AASHTO M 294. The joint shall be watertight according to the requirements of ASTM D 3212. Gaskets shall be made of polyisoprene meeting the requirements of ASTM F 477 with the addition that the gaskets shall not have any visible cracking when tested according to ASTM D 1149 after 72 hour exposure in 50 PPHM ozone at 104 degrees Fahrenheit. Gaskets shall be installed by the pipe manufacturer and covered with a removable wrap to ensure the gasket is free from debris. Joints shall remain watertight when subjected to a 1.5 degrees axial misalignment. A joint lubricant supplied by the manufacturer shall be used on the gasket and bell during assembly.

2.2	FITTINGS

1.	Polyvinyl Chloride (PVC) Fittings:  Polyvinyl chloride fittings shall be made from clean, virgin, PVC compound conforming to ASTM D 1784 and shall conform to the following requirements:

1)	Gravity Sewer:  Fittings shall be gasketed bell type provided by the same manufacturer as the pipe and conforming to ASTM D 3034 for SDR 35.

2)	Solvent Cement:  Solvent cement for use on PVC pipe and fittings shall conform to ASTM F 493 ASTM D 2564, or ASTM D 2846 as appropriate for pipe used.

2.	Ductile Iron Fittings:  Ductile iron fittings shall conform to AWWA C 104, AWWA C 110 for standard body and AWWA C 153 for compact body fittings, and meet the following requirements:

1)	Buried fittings shall be mechanical joint and supplied with the proper adapter and/or transition gasket for use with PVC pipe.

3.	Copper Pipe Fittings:  Fittings shall meet requirements of ANSI/ASME B 16.22 for wrought copper, sweat joint.

4.	Pressure Tubing Fittings:  Couplings and fittings for copper pressure tubing shall be bronze compression type similar to Ford Pack Joint or Grip Joint, or McDonald “T” series.

5.	Couplings:

1)	Flexible couplings for use in joining gravity pipe of differing materials and/or sizes shall be constructed of elastomeric polyvinyl chloride conforming to ASTM C 443, C 1173, D 5926 and secured to the connecting pipes using stainless steel screw type band clamps.  Flexible couplings shall be similar to Series 1056 as manufactured by Fernco, Inc., Series 151 as manufactured by Indiana Seal, Series MR as manufactured by mission Rubber Company, or approved equal.

6.	Restrained Joint Fittings:  If mechanical restraining glands are used as restraining mechanisms on joints, dimensions of the glands shall be such that they can be used with the standardized mechanical joint bell and tee head bolts conforming to the requirements of AWWA C 111 and AWWA C 153.

7.	High Density Polyethylene Fittings (Smooth Bore Pipe): Fittings shall conform to AASHTO M 294. Fabricated fittings shall be welded on the interior and exterior at all junctions.

2.3	Manholes

1.	General:  Concrete manholes shall be of precast construction.  All concrete shall be rodded or vibrated to minimize honeycombing and assure watertightness.  Items delivered and installed at the site shall be structurally sound and free from cracks or major surface blemishes.

2.	Construction:

1)	Precast manholes shall conform to ASTM C 478 and Standard Details as called for on the plans.  Drop manholes where required shall be constructed in accordance with Standard Detail MH-6.

2)	The eccentric design manhole shall be used, except as shown on the plans.

3)	Minimum inside diameter shall be 48 inches unless noted on plans, with minimum of 5 inch thick walls.  All manholes shall have monolithic bases except as shown on the plans.

4)	Precast inverts, when provided, shall comply with the requirements of paragraph 3.4.1 (Manholes) of this section.

3.	Manhole Steps:  Plastic steps only shall be provided in all manholes and shall be on 16 inch minimum centers.  Steps shall conform to Standard Detail MS-1.

4.	Pipe Connections:

1)	Provision for indicated storm drainage pipe connections shall be made by means approved in VDOT 302.

2)	Existing lines shall be grouted into place.

3)	The sewer line pipe shall be connected to the manhole base section with an approved flexible water-tight sleeve or gasket (similar to the New Lock Joint Flexible Manhole Sleeve as manufactured by the Interpace Corporation or the Z:LOK Manhole Pipe Connector as manufactured by A:LOK PRODUCTS INC.). The A:LOK Manhole Pipe Seal as manufactured by A:LOK CORP will not be an acceptable product for this purpose.

5.	Frames and Covers:  Frames and covers shall be of cast iron conforming to ASTM A 48 for Class 30 Gray Iron and shall meet the requirements of Standard Detail on the plan sheets.

6.	Concrete:  Concrete used for shaping of manholes, channels, sidewalk, and miscellaneous work shall meet requirements of VDOT Section 217 type A3.

7.	Joints:  Joints shall be sealed with two rings of butyl rubber rope conforming to AASHTO M 198, Type B.

Part 3 - execution

3.1	EXCAVATION, backfilling and compaction

1.	General:  Trench excavation shall be in accordance with Section 02317 – Excavation, Trenching, and Backfilling for Utilities.

3.2	separation of water and sewer lines

1.	Parallel Installation:

1)	Normal conditions – Water mains shall be separated at least 10 feet horizontally from a sewer or sewer manhole.  The distance shall be measured edge-to-edge.

2)	Unusual conditions – When local conditions prevent a horizontal separation of 10 feet, the CONTRACTOR shall notify the ENGINEER.  The ENGINEER, after consultation with the Virginia Department of Health, shall provide special instructions for construction within the area of conflict.  In some cases, if authorized by the ENGINEER, the 10 foot separation requirement may be waived provided that:

a)	The bottom (invert) of the water main shall be at least 18 inches above the top (crown) of the sewer.

b)	Where this vertical separation cannot be obtained, the sewer shall be constructed of AWWA approved water pipe, pressure tested in place to 30 psi without leakage prior to backfilling.

c)	The sewer manhole shall be of watertight construction and tested in place.

2.	Crossings:

1)	Normal conditions – Water lines crossing over sewers shall have a separation of at least 18 inches between the bottom of the water line and the top of the sewer.

2)	Unusual conditions – When local conditions prevent a vertical separation described above, the CONTRACTOR shall notify the ENGINEER.  The ENGINEER, after consultation with the Virginia Department of Health, shall provide special instructions for construction within the area of conflict.  In some cases, if authorized by the ENGINEER, the following construction shall be used:

a)	Sewers passing over or under water mains shall be constructed of AWWA approved water pipe, pressure tested in place to 30 psi without leakage prior to backfilling.

b)	Water lines passing under sewers shall, in addition, be protected by providing:

-	A vertical separation of at least 18 inches between the bottom of the sewer and the top of the water line.

-	Adequate structural support for the sewers to prevent excessive deflection of the joints and the settling on and breaking of the waterline.

-	That the length of the water line be centered at the point of the crossing so that joints shall be equidistant and as far as possible from the sewer.

3.	Intersections:  No water pipe shall pass through or come in contact with any part of the sewer or sewer manhole.

4.	Special Cases:  In the event that existing utilities or field conditions make it impossible or impractical to meet the separation requirements, the CONTRACTOR shall notify the ENGINEER.  The ENGINEER, after consultation with the Virginia Department of Health, shall provide special instructions for construction within the area of conflict.

3.3	INSTALLATION OF PIPE and FITTINGS

1.	General:  No valve, hydrant, or other appurtenance on existing water lines shall be opened or closed for any purpose by the CONTRACTOR.  Any opening or closing of valves, hydrants, whatsoever shall be by the OWNER of the utilities only.  The CONTRACTOR shall notify the OWNER of the utilities at least 24 hours prior to the need to open or close any appurtenance, except in emergencies, at which time the OWNER of the utilities shall be notified immediately.

2.	Handling:  Pipe shall be placed in the trench in such a manner as to prevent damage to pipe and protective coatings and linings.  Under no circumstances shall pipe be dropped or dumped into the trench.  As the temperature approaches or drops below freezing, extra care shall be used in handling pipe.

3.	Cleaning:  Every precaution shall be taken to prevent foreign material from entering the pipe while it is being placed in the line.  Spigot and bell ends of pipe and gaskets shall be cleaned and lubricated according to manufacturer's instructions.  At times when pipe laying is not in progress, the open ends of the pipe shall be closed by a watertight plug.

4.	Cutting:  Pipe shall be cut in a neat and workmanlike manner without damage to the pipe.  Unless otherwise authorized by the ENGINEER, cutting shall be done by means of approved type of mechanical cutters.  Wheel cutters shall be used when practicable.

5.	Direction of Laying:  All pipe shall be laid with bell ends facing in the direction of laying.  Where pipe is laid on a grade of 10 percent or greater, or for gravity pipe systems, the laying shall start at bottom and shall proceed upward with the bell ends of pipe upgrade.  Each piece of pipe shall be laid true to line and grade.  The bottom of the trench shall be smoothly graded and bell holes provided so that the trench bottom provides uniform support to the barrel of the pipe when in final position.  Adjustments to line or grade shall be made by removing or adding granular material under the barrel.  In no case shall wedges or blocks be used under the body of the pipe.  The pipe shall be pushed fully "home" by hand, with a bar and block of wood to cushion the bell, or other methods for large diameter pipe.

6.	Bedding:  Bedding of pipe shall be placed to the depth shown on the plans or standard details and shall be compacted to specified density.  Bedding of ductile iron and PVC pressure pipe will not be required except when used as gravity sewer, in rock excavation, or as shown on the plans.

1)	Special care must be taken during installation of ultra-rib pipe to insure ribs are completely imbedded in the bedding material to prevent settling after installation.  This material (sometimes referred to as “haunching”) from the bedding to the springline must be rodded with bars or consolidated with shovels to assure complete filling of the voids between each rib.  If pipe is completely covered with bedding/haunching material the same procedures shall be followed to prevent any voids between the pipe ribs.

7.	Lateral Connections: In-Line wyes and tees for cleanouts/laterals shall be installed during initial construction.  When lines are required to be tapped, connections shall be made using an approved watertight saddle.  Tapping into the ultra-rib pipe with the wye tapping saddle or the Fowler Inserta Tee will only be authorized to accommodate additional requirements subsequent to acceptance of project by the owner or as explicitly authorized by the Engineer.

8.	Anchorage:  For pipe installation at grades over 20 percent, the pipe shall be anchored in accordance with Standard Detail on the plan sheets.

9.	Deflection at Joints:  Maximum deflection for force main and pressure pipe joints will be as follows:

| Allowable Deflection (in inches) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pipe Size |  | Ductile Iron (Push on) Lengths 12' 16' 18' 20' |  |  |  |  | Ductile Iron (Mechanical) Lengths 12' 16' 18' 20' |  |  |  |  | PVC-AWWA (Push-on) |
| 4" |  | 12 | 17 | 19 | 21 |  | 21 | 28 | 31 | 34 |  | 12 |
| 6" |  | 12 | 17 | 19 | 21 |  | 18 | 24 | 27 | 30 |  | 4 |
| 8" |  | 12 | 17 | 19 | 21 |  | 13 | 18 | 20 | 22 |  | 3 |
| 10" |  | 12 | 17 | 19 | 21 |  | 13 | 18 | 20 | 22 |  | 2.5 |
| 12" |  | 12 | 17 | 19 | 21 |  | 13 | 18 | 20 | 22 |  | 2 |
| 16" |  | 7.5 | 10 | 11 | 12 |  | 9 | 12 | 13.5 | 15 |  | - |

1)	Flexible pipe may be curved in the trench to the limits specified in “Allowable Deflection (in inches table above)”.  Do not deflect PVC pipes in joints.  Joints must be secured laterally in ditch and deflection effected in the barrel of the pipe unless specific allowance by manufacturer is provided in the joint.

10.	Installation of Fittings:  Fittings shall be installed with the same care that mainline pipe is installed.  Caps or plugs shall be braced to prevent blow off during testing.

11.	Jointing:

1)	Mechanical Joints:  When installing mechanical joint (MJ) ductile iron pipe, the socket, spigot end and rubber gasket shall be thoroughly washed with soapy water to remove any grease or grit that might damage the gasket.  In making up the joint, the gland for MJ pipe followed by the gasket, shall be placed over the plain end of the pipe and inserted into the socket.  The gasket shall be pushed into position without excessive force and evenly seated in the socket of the pipe bell, and the gland for MJ pipe, then moved into position against the face of the rubber gasket.

2)	All joints within casing pipe shall be restrained.

12.	Installation of Tees and Laterals:  Tees and laterals shall be installed with the same care that mainline sewers are laid.  Slopes shall be not less than 1 percent unless otherwise indicated.  Laterals shall be of 4 inch or 6 inch pipe of the same material as the main sewer pipe and shall run to property lines unless otherwise indicated on the plans.  Laterals shall be properly capped and suitably sealed to prevent infiltration of water into the connections.  Caps or plugs shall be braced to prevent blowoff during exfiltration or air testing.  Ends of laterals shall be marked by a steel marker driven flush with the ground and in such a manner as to brace the plug on the lateral.  Couplings shall be provided as needed for ductile iron pipe connections to plastic tees.  Rotation of mainlines and concrete support will be required for deeper installations. Cleanouts per the appropriate detail shall be provided at the terminal points.  See Standard Detail on the plan sheets.

13.	Installation of Manhole Stubouts:  Manhole stubouts shall be provided where indicated or directed.  Stubout pipe shall be 8 inch diameter unless otherwise indicated on the plans and shall be the same pipe material as the sewer pipe.  Stubouts shall be sealed, braced and marked as noted for tees and laterals.

14.	Cleanouts:  Piping and fittings shall be constructed of the same materials as the main line sewer and shall conform to the appropriate Standard Detail CO-series.  Reconnecting to existing laterals shall be accomplished with proper water tight transition couplings as required.

15.	Setting of Valves:  Valves shall be installed in accordance with manufacturer's instructions and shall be in accordance with Section 02085 - Valves and Cocks and as shown on the Standard Details.

16.	Anchorage:  Pressure pipe lines shall be protected against joint pulling or thrust damage by suitable concrete anchors, braces, tie rods or mechanical joint restraining devices installed at direction changes as a result of fittings and all other critical points.

1)	Rods and clamps shall be galvanized or otherwise rust proof treated.

2)	Concrete anchors shall be of the size indicated in Standard Details on the plan sheets and shall bear on solid undisturbed earth.

3.4	manhole installation

1.	Manholes:  The subgrade and bedding for the monolithic base for the precast manhole shall be prepared similar to that for pipe.  The invert channels shall be formed with concrete as shown on Standard Details on plan sheets shall be smooth and semi-circular in shape, conforming to the inside of the adjacent sewer section.  Channel inverts shall be constructed to provide a smooth continuous positive slope between pipes.  Changes in direction of flow (horizontally and vertically) shall be made with a smooth curve of as large a radius as size of the manhole will permit as shown on Standard Details.  The floor (bench) of the manhole outside of the channels shall be smooth and shall slope toward the channels not less than 2 inches per foot nor more than 4 inches per foot. Under no circumstances shall manholes or other structures be left in an incomplete condition such that surface water could enter into the sewer line.

2.	Joints:  Joints shall be a double ring of butyl rubber rope caulk to form a watertight seal.  Manhole frames, covers, and hatches shall also be set on a double ring of butyl rubber rope caulk.  When leveling is required manhole frames shall be set level on a full bed of mortar installed to the proper grade and cured prior to the application of the butyl caulk.

3.5	Pipeline TESTING

1.	General:  Testing of pipe lines and structures shall be at the CONTRACTOR’s expense.  Any defects or leaks shall be repaired or replaced at the CONTRACTOR’s expense.  Water for the first test shall be provided by the OWNER.  Subsequent water for tests shall be at the CONTRACTOR’s expense.

2.	Pressure Testing:

1)	Test Section:  Pressure and leakage testing shall be conducted on each valved section (between adjacent valves) of pressure pipeline.

2)	Procedures:  Pressurization, air removal, and allowances shall be in accordance with AWWA C 600, Section 5 or AWWA C 605, Section 7 as appropriate for pipe used.  Testing shall begin on the first valved section of line within ten days after its completion.  The pressure and leakage tests shall be conducted concurrently for a duration of two hours.  Testing through fire hydrants shall not be permitted.  The valved section of the pipe under consideration shall be slowly filled with water and brought to the specified pressure by means of a pump.  Before supplying the specified test pressure, all air shall be expelled from the pipe.  Testing shall not begin until at least seven days after the last concrete anchor has been poured on the section of line being tested (if high early concrete is used, two days).  The Resident Project Representative shall observe all leakage tests.  If the pipe fails to meet test requirements, all leaks shall be repaired and defective pipe replaced at the CONTRACTOR’s expense.  The test shall be repeated until satisfactory results are obtained.  The CONTRACTOR shall be charged for all retests at the normal rates for inspection services.

3)	Test Pressures:  Test pressure shall be 150 psi unless otherwise noted.  For test pressures less than 200 psi, CONTRACTOR shall demonstrate that there is no significant pressure (other than static) in the adjacent sections of pipeline to the one being tested.

4)	Leakage:  Leakage shall be defined as the quantity of water that must be supplied into the valved pipe section to maintain pressure within 5 psi of the specified test pressure.  The allowable leakage shall not exceed the values given in table labeled Allowable Leakage Per 1,000 Feet of Pipeline.

Allowable Leakage Per 1,000 Feet (305 m) of ductile iron or 1111 feet (339 m) of PVC Pipeline - gph (multiply by 2 for 2 hour test)

| Avg. Test Pressure |  |  |  | Pipe Diameter |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| psi |  | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 |
| 300 |  | 0.39 | 0.52 | 0.78 | 1.04 | 1.30 | 1.56 | 1.82 | 2.08 | 2.34 | 2.60 | 3.12 |
| 275 |  | 0.37 | 0.50 | 0.75 | 1.00 | 1.24 | 1.49 | 1.74 | 1.99 | 2.24 | 2.49 | 2.99 |
| 250 |  | 0.36 | 0.47 | 0.71 | 0.95 | 1.19 | 1.42 | 1.66 | 1.90 | 2.14 | 2.37 | 2.85 |
| 225 |  | 0.34 | 0.45 | 0.68 | 0.90 | 1.13 | 1.35 | 1.58 | 1.80 | 2.03 | 2.25 | 2.70 |
| 200 |  | 0.32 | 0.43 | 0.64 | 0.85 | 1.06 | 1.28 | 1.48 | 1.70 | 1.91 | 2.12 | 2.55 |
| 175 |  | 0.30 | 0.40 | 0.59 | 0.80 | 0.99 | 1.19 | 1.39 | 1.59 | 1.79 | 1.98 | 2.38 |
| 150 |  | 0.28 | 0.37 | 0.55 | 0.74 | 0.92 | 1.10 | 1.29 | 1.47 | 1.66 | 1.84 | 2.21 |
| 125 |  | 0.25 | 0.34 | 0.50 | 0.67 | 0.84 | 1.01 | 1.18 | 1.34 | 1.51 | 1.68 | 2.01 |
| 100 |  | 0.23 | 0.30 | 0.45 | 0.60 | 0.75 | 0.90 | 1.05 | 1.20 | 1.35 | 1.50 | 1.80 |

3.	Gravity Sewer Testing:  All gravity sewer lines (except storm sewer) shall be tested by any or all of the following methods for both displacement or structural faults and for watertightness by the CONTRACTOR.  The testing methods shall be at the option of the ENGINEER.  The CONTRACTOR shall make all preparations and shall supply the labor for all tests.  The CONTRACTOR shall supply specialized equipment, such as T.V. cameras for the conduction of such tests.  No charge shall be made for initial witnessing of tests, but each succeeding test required on the same section of line caused by failure of the tests shall be charged to the CONTRACTOR.

1)	Pipe Displacement Testing - Lights:  A light will be flashed between manholes by means of a flashlight or by reflecting sunlight with a mirror.  If the illuminated interior of the pipeline shows visible leaks, poor alignment, displaced pipe or any other defects, they will be remedied by the CONTRACTOR at the CONTRACTOR’s expense.

2)	Pipe Displacement and Structural Testing - T.V.:  A T.V. camera to be supplied by the CONTRACTOR may be used to locate defects in the pipeline.  These shall then be remedied by the CONTRACTOR at the CONTRACTOR’s expense.

3)	Pipe Deflection Testing:  Pipe may be measured for vertical ring deflection after completion of the backfill.  Maximum ring deflection of the pipe under load shall be limited to 5.0 percent of the vertical internal pipe diameter.  Testing shall be accomplished by recording deflectometer or by approved mandrel, sphere, or pin type go/no-go device.  Such equipment shall be furnished by the CONTRACTOR.

4)	Pipe Air Testing:  Air Testing shll be conducted in accordance with ASTM F 1417 and as summarized below.

a)	Clean pipe to be tested by propelling snug-fitting inflated rubber ball through the pipe with water if necessary.

b)	Plug all pipe outlets with suitable test plugs.  Brace each plug securely.

c)	If the pipe to be tested is submerged in ground water, insert a pipe probe by boring or jetting into the backfill material adjacent to the center of the pipe, and determine the pressure in the probe when air passes slowly through it.  This is the back pressure due to ground water submergence over the end of the probe.  All gauge pressures in the test should be increased by this amount.

d)	Add air slowly to the portion of the pipe installation under test until the internal air pressure is raised to 4.0 psig.

e)	After an internal pressure of 4.0 psig is obtained, allow at least two minutes for air temperature to stabilize, adding only the amount of air required to maintain pressure.

f)	After stabilizing the internal pressure at 4.0 psig, reduce the internal air pressure to 3.5 psig, and start stopwatch.  Determine the time in minutes and seconds that is required for the internal air pressure to reach 2.5 psig.  Minimum permissible pressure holding times for runs of single pipe diameter and for systems of 4 inch, 6 inch, or 8 inch laterals in combination with trunk lines are indicated in minutes and seconds in the table shown.

g)	NOTE:  The air test may be dangerous if, because of ignorance or carelessness, a line is improperly prepared.  It is extremely important that the various plugs be installed and braced in such a way as to prevent blowouts.  In as much as a force of 250 pounds is exerted on an 8 inch plug by an internal pipe pressure of 5 psi, it should be realized that sudden expulsion of a poorly installed plug or of a plug that is partially deflated before the pipe pressure is released can be dangerous.  As a safety precaution, pressurizing equipment should include a regulator set at perhaps 10 psi to avoid over pressurizing and damaging an otherwise acceptable line.  No one shall be allowed in the manholes during testing.  The pressure gauge used during the test shall be located completely outside of manhole.

| 1 Pipe Dia. (in.) | 2 Minimum Time (min:sec) |  |  | 3 Length for Minimum Time (ft.) |  | 4 Time for Longer Length (sec) |  | Specification Time for Length (L) Shown (min:sec) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | 100' |  | 150' | 200' | 250' | 300' | 350' | 400' | 450' |
| 4 |  | 3:46 | 597 |  | .380 L |  | 3:46 |  | 3:46 | 3:46 | 3:46 | 3:46 | 3:46 | 3:46 | 3:46 |
| 6 |  | 5:40 | 398 |  | .854 L |  | 5:40 |  | 5:40 | 5:40 | 5:40 | 5:40 | 5:40 | 5:42 | 6:24 |
| 8 |  | 7:34 | 298 |  | 1.520 L |  | 7:34 |  | 7:34 | 7:34 | 7:34 | 7:36 | 8:52 | 10:08 | 11:24 |
| 10 |  | 9:26 | 239 |  | 2.374 L |  | 9:26 |  | 9:26 | 9:26 | 9:53 | 11:52 | 13:51 | 15:49 | 17:48 |
| 12 |  | 11:20 | 199 |  | 3.418 L |  | 11:20 |  | 11:20 | 11:24 | 14:15 | 17:05 | 19:56 | 22:47 | 25:38 |
| 15 |  | 14:10 | 159 |  | 5.342 L |  | 14:10 |  | 14:10 | 17:48 | 22:15 | 26:42 | 31:09 | 35:36 | 40:04 |
| 18 |  | 17:00 | 133 |  | 7.692 L |  | 17:00 |  | 19:13 | 25:38 | 32:03 | 38:27 | 44:52 | 51:16 | 57:41 |
| 21 |  | 19:50 | 114 |  | 10.470 L |  | 19:50 |  | 26:10 | 34:54 | 43:37 | 52:21 | 61:00 | 69:48 | 78:31 |
| 24 |  | 22:40 | 99 |  | 13.674 L |  | 22:47 |  | 34:11 | 45:34 | 56:58 | 68:22 | 79:46 | 91:10 | 102:33 |
| 27 |  | 25:30 | 88 |  | 17.306 L |  | 28:51 |  | 43:16 | 57:41 | 72:07 | 86:32 | 100:57 | 115:22 | 129:48 |
| 30 |  | 28:20 | 80 |  | 21.366 L |  | 35:37 |  | 53:25 | 71:13 | 89:02 | 106:50 | 124:38 | 142:26 | 160:15 |
| 33 |  | 31:10 | 72 |  | 25.852 L |  | 43:05 |  | 64:38 | 86:10 | 107:43 | 129:16 | 150:43 | 172:21 | 193:53 |
| 36 |  | 34:00 | 66 |  | 30.768 L |  | 51:17 |  | 76:55 | 102:34 | 128:12 | 153:50 | 179:29 | 205:07 | 230:46 |

3.6	manhole testing

1.	Manhole Vacuum Testing:  Unless otherwise approved by the Engineer, manholes shall be tested by the vacuum method.  Stubouts, manhole boots and pipe plugs shall be secured to prevent movement while the vacuum is drawn.  Installation and operation of vacuum equipment and indicating devices shall be in accordance with equipment specifications for which performance information has been provided by the manufacturer and approved by the Virginia Department of Environmental Quality.  A measured vacuum of 10 inches of mercury shall be established in the manhole.  The time for the vacuum to drop to nine inches of mercury shall be recorded.

1)	Acceptance standards for leakage shall be established from the elapsed time for a negative pressure change from 10 inches to 9 inches of mercury.  The maximum allowable leakage rate shall be in accordance with ASTM C 1244.

#### TABLE 1 – Minimum Test Times for Various Manhole Diameters in Seconds

| #### Diameter, in. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| #### Depth (ft) | #### 30 | #### 33 | #### 36 | #### 42 | #### 48 | #### 54 | #### 60 | #### 66 | #### 72 |
| #### Time, in seconds |  |  |  |  |  |  |  |  |  |
| #### 8 | #### 11 | #### 12 | #### 14 | #### 17 | #### 20 | #### 23 | #### 26 | #### 29 | #### 33 |
| #### 10 | #### 14 | #### 15 | #### 18 | #### 21 | #### 25 | #### 29 | #### 33 | #### 36 | #### 41 |
| #### 12 | #### 17 | #### 18 | #### 21 | #### 25 | #### 30 | #### 35 | #### 39 | #### 43 | #### 49 |
| #### 14 | #### 20 | #### 21 | #### 25 | #### 30 | #### 35 | #### 41 | #### 46 | #### 51 | #### 57 |
| #### 16 | #### 22 | #### 24 | #### 39 | #### 34 | #### 40 | #### 46 | #### 52 | #### 58 | #### 67 |
| #### 18 | #### 25 | #### 27 | #### 32 | #### 38 | #### 45 | #### 52 | #### 59 | #### 65 | #### 73 |
| #### 20 | #### 28 | #### 30 | #### 35 | #### 42 | #### 50 | #### 53 | #### 65 | #### 72 | #### 81 |
| #### 22 | #### 31 | #### 33 | #### 39 | #### 46 | #### 55 | #### 64 | #### 72 | #### 79 | #### 89 |
| #### 24 | #### 33 | #### 36 | #### 42 | #### 51 | #### 59 | #### 64 | #### 78 | #### 87 | #### 97 |
| #### 26 | #### 36 | #### 39 | #### 46 | #### 55 | #### 64 | #### 75 | #### 85 | #### 94 | #### 105 |
| #### 28 | #### 39 | #### 42 | #### 49 | #### 59 | #### 69 | #### 81 | #### 91 | #### 101 | #### 113 |
| #### 30 | #### 42 | #### 45 | #### 53 | #### 63 | #### 74 | #### 87 | #### 98 | #### 108 | #### 121 |

1)	If the manhole fails the test, necessary repairs shall be made and the vacuum test and repairs shall be repeated until the manhole passes the test or the manhole shall be tested in accordance with the standard exfiltration test and rated accordingly.

2)	If a manhole joint material is pulled out during the vacuum test, the manhole shall be retested after it is disassembled and the mastic replaced.

3.7	DISINFECTION

1.	General:  Disinfection of water mains shall be in accordance with Section 02510 - Water Distribution.

3.8	exposed PIPING IDENTIFICATION

1.	General: To identify exposed piping, the different lines shall have contrasting colors.  Pipes shall be color coded in a manner that will permit ready identification of pipes at any location.  Labeling of the identification of the pipe with or without an accompanying color code shall be considered as an acceptable substitute for the color scheme contained herein.  Where color bands are utilized, the bands are to be one-inch wide and placed on 18 inch centers.

#### Sludge Line - Dark Brown
Gas Line - Red
Potable Water Line - Dark Blue
Chlorine Line - Yellow
Sewage Line - Dark Gray
Compressed Air Line - Dark Green
Water Line for Heating Digestors or Building - Dark Blue with Red Band
Oxygen - White with Red Band
Non Potable Water Line - Light Gray with Yellow Band

END OF SECTION