SECTION 02510

Water distribution

PART 1 - GENERAL

1.1	Description

1.	Work Included:  Furnish all labor, materials, tools, transportation, supplies, equipment, testing, and disinfection of the water main shown on the plans.

2.	Related Sections:  Additional Sections of the Documents which are referenced in this Section include:

1)	Section 02080 - Utility Pipe and Materials

2)	Section 02085 - Valves and Cocks

1.2	REFERENCES

1.	General:  The work shall comply with the most recent standards or tentative standards as published at the date of the contract and as listed in this specification using the abbreviation shown.

2.	American National Standards Institute (ANSI)/American Water Works Association (AWWA):

1)	C 651	Standard for Disinfecting Water Mains

1.3	quality assurance

1.	Contractor Responsibilities:  Use adequate numbers of skilled workmen who are thoroughly trained and experienced in the necessary crafts and who are completely familiar with the specified requirements and the methods needed for proper performance of the work in this section.

1.4	delivery, storage, and handling

1.	General:  Shall be in accordance with Division I requirements.

PART 2 - products

2.1	materials

1.	Pipe and Fittings, Joints, and Coating:  All materials shall be in accordance with the Section 02080 - Utility Pipe and Materials.

2.	Valves:  All valves shall be in accordance with Section 02085 - Valves and Cocks.

3.	Concrete:  Miscellaneous concrete shall be VDOT Type A-3 specifications.

4.	Tie Rods:  ¾ inch thread steel rods for hydrant clamping shall be galvanized or otherwise rustproof treated.  Compatible tie bolts and nut or clamps shall be similarly rustproof treated.

PART 3 - execution

3.1	installation of pipe, fittings, and accessories

1.	Pipe and Fitting Installation:  All work shall be in accordance with Section 02080 - Utility Pipe and Materials.

2.	Valve Installation:  All work shall be in accordance with Section 02085 - Valves and Cocks.

3.2	disinfection

1.	Disinfecting Water Mains:  Water mains and accessories shall be disinfected using the “continuous-feed” or “slug method” in accordance with ANSI/AWWA C 651.  The “Tablet Method” described in ANSI/AWWA C 651 shall not be used.  The successful bidder shall obtain the most recent applicable AWWA standard.  This standard shall be at jobsite with access granted to Resident Project Representative and owner. Care shall be taken to minimize entrance of foreign material into pipe, fittings and valves. The main shall be flushed prior to disinfection with sufficient flow to produce a velocity of 2.5 fps. Flushing shall take place in areas with adequate drainage.

1)	Final flushing shall follow to ensure that the chlorine concentration is not higher than that generally prevailing in the system.  Chlorinated water shall not be discharged to any water course or drainage way until it is diluted or reduced to a level which will result in no damage to aquatic life.

2.	Bacteriological Tests:  After final flushing and before the water main is placed in service, 2 consecutive samples shall be collected at 24 hours intervals for each 2000 feet of line. These samples shall be tested for bacteriological quality by the State Laboratory or other certified laboratory and shall show the absence of coliform organisms.  Samples will be collected (through the use of sample taps supplied by the CONTRACTOR) and delivered to the Testing Laboratory by the OWNER within 48 hours of written notifications from CONTRACTOR.  If the initial disinfection fails to produce satisfactory samples, disinfection shall be repeated until satisfactory samples have been obtained.  The CONTRACTOR is responsible for the cost of all tests.

END OF SECTION